## CUNY Emissions OLD
Emission Calculations based on CEQR Appendix and AP-42
Emission Factors
| Boilers - Oil | Boilers - NG | Microturbine - NG |  |  | NG | 1031 | BTU/ft3 | 30 | ppm
| lb/MMBtu | lb/MMBtu |  |  |  |  | 9.5 | kW/Nm3 | 1.19e-07 | ppm to lb/dscf @ 0% O2
NOx | 0.14286 | 0.036306 | 500 | mg/Nm3 |  | #2 Oil | 140 | MMBTU/103gal | 8710 | Fuel conversion factor
PM10 | 0.023571 | 0.0073715 | 0.0099871 | lb/MMBtu | AP-42 Table 3.2-2 |  |  |  | 3 | %O2
PM2.5 | 0.023571 | 0.0073715 | 0.0099871 | lb/MMBtu | AP-42 Table 3.2-2
SO2 | 0.0015214 | 0.00058196 | 0.000588 | lb/MMBtu | AP-42 Table 3.2-2 |  |  |  | 0.036306 | lb/mmBtu
| AP-42 Table 1.3-1 | AP-42 Table 1.4-1
| AP-42 Table 1.3-2 | AP-42 Table 1.4-2
sulfur content of 15ppm (0.0015 percent) (6NYCRR Subpart 225-1.2)
|  |  | #2 Oil | Natural Gas | Natural Gas
| Building | Units | Boilers |  | Microturbine
| X Coordinate | (m)
| Y Coordinate | (m)
| Number of Units | - | 4 |  | 1
| Power Rating | MBTU/hr | 6000
|  | kW |  |  | 1063
| Daily Load Average |  | 70% |  | 100%
| Efficiency |  | 82%
Annual Periods | Heat Input | MMBtu/hr | 20.4878 |  | 8.9034
| Fuel Consumption | NG (Nm3/hr) |  |  | 274.4211
|  | Oil (gal/hr) | 146.3415
| Stack Diameter | (m) | 1.2192 |  | 0.2032
| Stack Height | (ft) | 349 |  | 322
|  | (m) | 106.3752 |  | 98.1456
| Exhaust Flow rate | scfm | - |  | 2583.2681
| Exhaust Flow rate | acfm | - |  | 2980.9234
| Temperature2 | (K) | 307.8 |  | 723.15
| Velocity2 | (m/s) | 7.2304 |  | 43.3818
| Velocity | (ft/s) | 23.7219 |  | 142.3356
| Nox | g/s
| PM10 | g/s | 0.060847 | 0.019029 | 0.011204
| PM2.5 | g/s | 0.060847 | 0.019029 | 0.011204
| SO2 | g/s
<= 24 Hr Periods | Heat Input | MMBtu/hr | 29.2683 |  | 8.9034
| Stack Diameter | (m) | 1.2192 |  | 0.2032
| Stack Height | (ft) | 349 |  | 322
|  | (m) | 106.3752 |  | 98.1456
| Exhaust Flow rate | scfm |  |  | 2583.2681
| Exhaust Flow rate | acfm |  |  | 2980.9234
| Temperature2 | (K) | 307.8 |  | 723.15
| Velocity2 | (m/s) | 77.8276 |  | 43.3818
| Velocity | (ft/s) | 23.7219 |  | 142.3356
| Nox | g/s | 0.52682 | 0.13389 | 0.038114
| PM10 | g/s | 0.086925 | 0.027184 | 0.011204
| PM2.5 | g/s | 0.086925 | 0.027184 | 0.011204
| SO2 | g/s | 0.0056106 |  | 0.00065284
Nox emission rate calculation using Vendor data
Nox emissions = 30 ppm (provided)
lbs/mmBtu = ppm*Cd*Fd*(20.9/(20.9-%O2))
Cd is a conversion factor from ppm to lb/dscf at 0% O2 and is specific per pollutant.
Fd is the fuel F conversion factor which is 8710 for natural gas (I don't have it off the top of my head for fuel oil)
So at 70 ppm at 4% O2:
lbs/mmBtu = 12*1.191E-07*8710*(20.9/(20.9-4)) = 0.044 lbs/mmBtu

## MSK Emissions OLD
Emission Calculations based on CEQR Appendix and AP-42
Emission Factors
| Boilers - Oil | Boilers - NG | Cogen - NG |  |  | NG | 1031 | BTU/ft3 |  | 30 | ppm
| lb/MMBtu | lb/MMBtu |  |  |  |  | 9.5 | kW/Nm3 |  | 1.19e-07 | ppm to lb/dscf @ 0% O2
NOx | 0.14286 | 0.036306 | 500 | mg/Nm3 |  | #2 Oil | 140 | MMBTU/103gal |  | 8710 | Fuel conversion factor
PM10 | 0.023571 | 0.0073715 | 0.0099871 | lb/MMBtu | AP-42 Table 3.2-2 |  |  |  |  | 3 | %O2
PM2.5 | 0.023571 | 0.0073715 | 0.0099871 | lb/MMBtu | AP-42 Table 3.2-2
SO2 | 0.0015214 | 0.00058196 | 0.000588 | lb/MMBtu | AP-42 Table 3.2-2 |  |  |  |  | 0.036306 | lb/mmBtu
| AP-42 Table 1.3-1 | AP-42 Table 1.4-1
| AP-42 Table 1.3-2 | AP-42 Table 1.4-2 | [5 empty] | 24-Hour Mixes
| sulfur content of 15ppm (0.0015 percent) (6NYCRR Subpart 225-1.2) | [6 empty] | Hours Oil | Effective Emission Rate
[8 empty] | 0 | 0.037916
|  |  | #2 Oil | Natural Gas | Natural Gas |  |  | 1 | 0.041388
| Building | Units | Boilers | Boilers | Cogen |  |  | 2 | 0.04486
| X Coordinate | (m) | [5 empty] | 3 | 0.048332
| Y Coordinate | (m) | [5 empty] | 4 | 0.051804
| Number of Units | - | 2 |  | 1 |  |  | 5 | 0.055276
| Power Rating | BHP | 500 |  |  |  |  | 6 | 0.058748
|  | kW | 4905.5 |  | 1063 |  |  | 7 | 0.062219
| Daily Load Average |  | 70% |  | 100% |  |  | 8 | 0.065691
| Efficiency |  | 82% |  |  |  |  | 9 | 0.069163
Annual Periods | Heat Input | MMBtu/hr | 28.5762 |  | 8.9034 |  |  | 10 | 0.072635
| Fuel Consumption | NG (Nm3/hr) |  |  | 274.4211 |  |  | 11 | 0.076107
|  | Oil (gal/hr) | 204.1159 |  |  |  |  | 12 | 0.079579
| Stack Diameter | (m) | 0.8621 |  | 0.2032 |  |  | 13 | 0.083051
| Stack Height | (ft) | 449 |  | 449 |  |  | 14 | 0.086523
|  | (m) | 136.8552 |  | 136.8552 |  |  | 15 | 0.089995
| Exhaust Flow rate | scfm | - |  | 2583.2681 |  |  | 16 | 0.093467
| Exhaust Flow rate | acfm | - |  | 2980.9234 |  |  | 17 | 0.096939
| Temperature2 | (K) | 307.8 |  | 723.15 |  |  | 18 | 0.10041
| Velocity2 | (m/s) | 5.9371 |  | 43.3818 |  |  | 19 | 0.10388
| Velocity | (ft/s) | 19.4786 |  | 142.3356 |  |  | 20 | 0.10735
| Nox | g/s | [5 empty] | 21 | 0.11083
| PM10 | g/s | 0.08487 | 0.026541 | 0.011204 |  |  | 22 | 0.1143
| PM2.5 | g/s | 0.08487 | 0.026541 | 0.011204 |  |  | 23 | 0.11777
| SO2 | g/s | [5 empty] | 24 | 0.12124
<= 24 Hr Periods | Heat Input | MMBtu/hr | 40.8232 |  | 8.9034
| Stack Diameter | (m) | 0.8621 |  | 0.2032
| Stack Height | (ft) | 449 |  | 449
|  | (m) | 136.8552 |  | 136.8552
| Exhaust Flow rate | scfm |  |  | 2583.2681
| Exhaust Flow rate | acfm |  |  | 2980.9234
| Temperature2 | (K) | 307.8 |  | 723.15
| Velocity2 | (m/s) | 63.9061 |  | 43.3818
| Velocity | (ft/s) | 19.4786 |  | 142.3356
| Nox | g/s | 0.7348 | 0.18674 | 0.038114
| PM10 | g/s | 0.12124 | 0.037916 | 0.011204
| PM2.5 | g/s | 0.12124 | 0.037916 | 0.011204
| SO2 | g/s | 0.0078256 |  | 0.00065284
Nox emission rate calculation using Vendor data
Nox emissions = 30 ppm (provided)
lbs/mmBtu = ppm*Cd*Fd*(20.9/(20.9-%O2))
Cd is a conversion factor from ppm to lb/dscf at 0% O2 and is specific per pollutant.
Fd is the fuel F conversion factor which is 8710 for natural gas (I don't have it off the top of my head for fuel oil)
So at 70 ppm at 4% O2:
lbs/mmBtu = 12*1.191E-07*8710*(20.9/(20.9-4)) = 0.044 lbs/mmBtu

## NYCDEP CA Permit
| Exit | Exit | Exit | Heat | Gross | Fuel
C_BOILER_MAKEMOD | Temp | Velocity | ACFM | Input | Btu | Type
| deg F | ft/sec | ft3/min | MMBtu/hr
FEDERAL FST 40 | 371 | 19 | 633 | 1.7 | 1.7 | 34
BEST 5A- 50 | 400 | 9 | 745 | 2 | 2 | 34
BEST BOILER CO 4A-55 | 450 | 8 | 853 | 2.3 | 2.3 | 34
FEDERAL FST-60 | 400 | 10 | 822 | 2.32 | 2.32 | 34
FEDERAL FST 70 | 128 | 10 | 674 | 2.6 | 2.59 | 34
PACIFIC 219 | 350 | 4 | 1072 | 2.7 | 2.7 | 34
WEIL MCLAIN BL 1088S | 400 | 12 | 1064 | 3.01 | 3.01 | 32
ROCKMILLS MP 80 | 215 | 21 | 1004 | 3.4 | 3.4 | 32
FEDERAL FST 80 | 288 | 10 | 1135 | 3.4 | 3.4 | 34
ROCKMILLS MP 80 | 266 | 10 | 1063 | 3.43 | 3.43 | 36
FEDERAL FST 100 | 150 | 5 | 1396 | 3.8 | 4.2 | 34
ROCKMILLS MP 100 | 228 | 3 | 1172 | 3.9 | 4.2 | 34
ROCKMILLS MP-90 | 292 | 5 | 1213 | 3.97 | 3.78 | 32
ROCKMILLS MODEL MP-100 | 240 | 3 | 1217 | 4 | 4.2 | 36
ROCKMILLS MP 150 | 400 | 3 | 1490 | 4 | 4 | 32
ROCKMILLS MP-100 | 261 | 2 | 1254 | 4.1 | 4.2 | 36
H.B. SMITH HB 2800 S14 | 400 | 5 | 1485 | 4.1 | 4.2 | 32
FEDERAL FST 100 | 304 | 12 | 1352 | 4.1 | 4.1 | 32
ROCKMILLS MP 100 (RIGHT SIDE) | 350 | 3 | 1491 | 4.3 | 4.3 | 34
ROCKMILLS MP 100 | 350 | 3 | 1491 | 4.3 | 4.3 | 34
FEDERAL FL1215 | 600 | 31 | 2102 | 4.6 | 4.6 | 34
ROCKMILLS MP125 | 400 | 3 | 1850 | 5 | 5 | 32
Average ACFM & dia (1 MMBtu to 5 MMBtu) |  |  | 1208.0909 |  |  |  | Exit Velocity with |  | 1 | foot diameter stack
FEDERAL FST 125 | 350 | 13 | 2082 | 5.3 | 5.3 | 34 | stack dia | stack vel | stack vel
FEDERAL FST-125 | 400 | 7 | 2211 | 5.3 | 5.3 | 36 | meters | ft/sec | m/sec
FEDERAL FST 70 | 350 | 8 | 2254 | 5.7 | 2.81 | 36 | 0.3048 | 25.6495 | 7.818 | use this data for model input
ROCKMILLS (NEW) MP-150 | 400 | 15 | 2054 | 5.81 | 5.81 | 36
FEDERAL FST-150 | 400 | 5 | 2202 | 6.23 | 6.23 | 34
BURNHAM (SPENCER) 3-150-50 | 350 | 19 | 2488 | 6.27 | 6.27 | 36
ROCKMILLS MP-150 | 247 | 9 | 1971 | 6.3 | 6.3 | 34
ROCKMILLS MP 175 | 400 | 12 | 2364 | 6.4 | 7.1 | 36
WEIL MCLAIN 1794 | 400 | 6 | 2277 | 6.4 | 6.4 | 34
FEDERAL FST-200 SP | 350 | 10 | 2732 | 6.9 | 6.9 | 36
ROCKMILLS MP 175 | 144 | 22 | 1871 | 7 | 7 | 36
FEDERAL FST-175 | 360 | 3 | 2569.24 | 7 | 7 | 36
FEDERAL FST 200 | 414 | 6 | 2365 | 7.7 | 7.7 | 34
WEIL MCLAIN BL-1586 | 350 | 17 | 3349 | 7.8 | 3.9 | 52
NEW FEDERAL FST 200 SP | 223 | 9 | 2348 | 7.8 | 7.8 | 36
FEDERAL FST 200 | 244 | 12 | 2420 | 7.8 | 7.8 | 36
ROCKMILLS R303 | 242 | 2 | 2427 | 7.8 | 7.8 | 34
FEDERAL FST-200 | 350 | 5 | 3249 | 8.2 | 8.2 | 34
FEDERAL FST-200 | 256 | 2 | 2595 | 8.2 | 8.2 | 36
FEDERAL FST-200 | 450 | 7 | 3181 | 8.2 | 8.2 | 32
FEDERAL FST-200 | 194 | 5 | 2390 | 8.3 | 8.3 | 34
ROCKMILLS MP-250 | 450 | 11 | 3417 | 9.3 | 9.3 | 36
FEDERAL FST 250 | 222 | 4 | 3004 | 10 | 10 | 34
Average ACFM & dia (5 MMBtu to 10 MMBtu) |  |  | 2513.9235 |  |  |  | Exit Velocity with |  | 1.5 | foot diameter stack
ROCMILLS MP-250 | 220 | 7 | 3007 | 10.36 | 10.36 | 36 | stack dia | stack vel | stack vel
ROCKMILLS MP 150 | 207 | 5 | 3512 | 11.9 | 5.95 | 34 | meters | ft/sec | m/sec
FEDERAL FST 150 | 203 | 4 | 3534 | 12 | 5.88 | 36 | 0.4572 | 23.7219 | 7.2304 | use this data for model input
FEDERAL FST-100 | 273 | 6 | 3837 | 12.26 | 4.2 | 36
H.B. SMITH 28-S-11 | 400 | 4 | 4520 | 12.58 | 3.08 | 32
CLEAVER BROOKS CB-400-350 | 94 | 2 | 3608.6 | 14 | 14 | 36
Average ACFM & dia (10 MMBtu to 15 MMBtu) |  |  | 3669.7667 |  |  |  | Exit Velocity with |  | 2 | foot diameter stack
HEGGIE SIMPLEX 328 | 300 | 4 | 6591 | 17.7 | 9.7 | 34 | stack dia | stack vel | stack vel
FEDERAL FST-250 | 400 | 8 | 7326 | 20.72 | 10.35 | 34 | meters | ft/sec | m/sec
CLEAVERBROOK CB 800 250 | 94 | 17 | 5128 | 20.9 | 10.45 | 34 | 0.6096 | 19.4786 | 5.9371 | use this data for model input
HEGGIE SIMPLEX #328 | 94 | 5 | 6024 | 25.87 | 12.94 | 34
FEDERAL FST 350 | 300 | 13 | 10317 | 27.7 | 14.7 | 36
FEDERAL FST-350 | 94 | 3 | 6919 | 28.2 | 28.2 | 36
ROCKMILLS MP-600 | 300 | 27 | 8888 | 35.1 | 25.2 | 36
HEINE W.T. 308 HP | 350 | 6 | 14494 | 36.5 | 12.04 | 34
HEINE WT 308 HP | 350 | 6 | 14494 | 36.5 | 12.5 | 34
Average ACFM & dia (15 MMBtu and up) |  |  | 8909 |  |  |  | Exit Velocity with |  | 3 | foot diameter stack
Average Temp (all boilers) | 307.8 | [5 empty] | stack dia | stack vel | stack vel
Max Temp | 600 | [5 empty] | meters | ft/sec | m/sec
Note: | [6 empty] | 0.9144 | 21.0167 | 6.4059 | use this data for model input
Exit velocity calculated from avg acfm & stack diameter: | Exit velocity = X ft3/min / 60 min/sec / stack sfc area in ft2
where: area = pi * ((dia/2)^2)
Boiler information obtained from NYCDEP CA Permit database. This data was used to calculate the average temperature of boiler gases exiting the stack.
The data was also used to calculate the average flowrate in acfm for specific ranges in boiler size. From these average values, the corresponding exit velocity
was calculated for each boiler size range using assumed stack diameters.

## CUNY Emissions
Emission Calculations based on CEQR Appendix and AP-42
Emission Factors
| Boilers - Oil | Boilers - NG |  | NG | 1031 | BTU/ft3 | 30 | ppm
| lb/MMBtu | lb/MMBtu |  |  | 9.5 | kW/Nm3 | 1.19e-07 | ppm to lb/dscf @ 0% O2
NOx | 0.14286 | 0.036306 | lb/MMBtu | #2 Oil | 140 | MMBTU/103gal | 8710 | Fuel conversion factor
PM10 | 0.023571 | 0.0073715 | lb/MMBtu |  |  |  | 3 | %O2
PM2.5 | 0.023571 | 0.0073715 | lb/MMBtu
SO2 | 0.0015214 | 0.00058196 | lb/MMBtu |  |  |  | 0.036306 | lb/mmBtu
| AP-42 Table 1.3-1 | 30ppm calc
| AP-42 Table 1.3-2 | AP-42 Table 1.4-2
sulfur content of 15ppm (0.0015 percent) (6NYCRR Subpart 225-1.2)
Natural Gas
| Building | Units | Boilers
| X Coordinate | (m)
| Y Coordinate | (m)
| Number of Units | - | 4
| Power Rating | MBTU/hr
kW
Efficiency
Annual Periods | Fuel Consumption | MMBtu/hr | 1.8734
NG (Nm3/hr)
Oil (gal/hr)
| Stack Diameter | (m) | 1.2192
|  | (fr) | 4
| Stack Height | (ft) | 332.25
|  | (m) | 101.2698
| Exhaust Flow rate | scfm | -
| Exhaust Flow rate | acfm | -
| Temperature2 | (K) | 426.3722
| Velocity2 | (m/s) | 7.2304
| Velocity | (ft/s) | 23.7219
| NOx | g/s | 0.0085698
| PM10 | g/s | 0.00174
| PM2.5 | g/s | 0.00174
24 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 3.1711
| PM10 | g/s | 0.0029453
| PM2.5 | g/s | 0.0029453
1 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 6.68
| NOx | g/s | 0.030557
| SO2 | g/s | 0.00048981
#2 Oil Factors
24 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 3.1711
| PM10 | g/s | 0.009418
| PM2.5 | g/s | 0.009418
1 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 6.68
| NOx | g/s | 0.12024
| SO2 | g/s | 0.0012805
Nox emission rate calculation using Vendor data
Nox emissions = 30 ppm (provided)
lbs/mmBtu = ppm*Cd*Fd*(20.9/(20.9-%O2))
Cd is a conversion factor from ppm to lb/dscf at 0% O2 and is specific per pollutant.
Fd is the fuel F conversion factor which is 8710 for natural gas (I don't have it off the top of my head for fuel oil)
So at 70 ppm at 4% O2:
lbs/mmBtu = 12*1.191E-07*8710*(20.9/(20.9-4)) = 0.044 lbs/mmBtu

## MSK Emissions
Emission Calculations based on CEQR Appendix and AP-42
Emission Factors
| Boilers - Oil | Boilers - NG | Cogen - NG |  |  | NG | 1031 | BTU/ft3 | 30 | ppm | 9 | ppm
| lb/MMBtu | lb/MMBtu |  |  |  |  | 9.5 | kW/Nm3 | 1.19e-07 | ppm to lb/dscf @ 0% O2 | 1.19e-07 | ppm to lb/dscf @ 0% O2
NOx | 0.14286 | 0.036306 | 0.010892 | lb/MMBtu |  | #2 Oil | 140 | MMBTU/103gal | 8710 | Fuel conversion factor | 8710 | Fuel conversion factor
PM10 | 0.023571 | 0.0073715 | 0.0066 | lb/MMBtu |  |  |  |  | 3 | %O2 | 3 | %O2
PM2.5 | 0.023571 | 0.0073715 | 0.0066 | lb/MMBtu
SO2 | 0.0015214 | 0.00058196 | 0.0034 | lb/MMBtu |  |  |  |  | 0.036306 | lb/mmBtu | 0.010892 | lb/mmBtu
| AP-42 Table 1.3-1 | AP-42 Table 1.4-1 | 9ppm calc
| AP-42 Table 1.3-2 | AP-42 Table 1.4-2 | AP-42 Table 3.2-2 | [7 empty] | 11400000 | BTU/hr | Capstone C1000 Fuel Flow
| sulfur content of 15ppm (0.0015 percent) (6NYCRR Subpart 225-1.2) | [9 empty] | 14.65 | lbm/s | Capstone C1000 Gas Flow
[11 empty] | 52740 | lbm/hr
|  |  | Natural Gas | Natural Gas
| Building | Units | Boilers | Cogen
| X Coordinate | (m)
| Y Coordinate | (m)
| Number of Units | - | 2 | 1
| Power Rating | BHP
|  | kW |  | 1000 | Capstone C1000
Daily Load Average
Annual Periods | Fuel Consumption | MMBtu/hr | 2.5595 | 11.4
NG (Nm3/hr)
Oil (gal/hr)
| Stack Diameter | (m) | 0.8621 | 0.68155 | (equivalent to x5 C200 exhaust diameters)
|  | (ft) | 2.8284 | 2.2361
| Stack Height | (ft) | 443 | 410
|  | (m) | 135.0264 | 124.968
| Exhaust Flow rate | scfm | - | 11708.28
| Exhaust Flow rate | acfm | - | 23710.1779
| Temperature2 | (K) | 426.3722 | 553.15 | Capstone C1000
| Velocity2 | (m/s) | 5.9371 | 30.6718
| Velocity | (ft/s) | 19.4786 | 100.634
| Nox | g/s | 0.011709 | 0.015645
| PM10 | g/s | 0.0023773 | 0.00948
| PM2.5 | g/s | 0.0023773 | 0.00948
24 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 8.0059 | 11.4
| PM10 | g/s | 0.0074358 | 0.00948
| PM2.5 | g/s | 0.0074358 | 0.00948
1 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 26.37 | 11.4
| NOx | g/s | 0.12063 | 0.015645
| SO2 | g/s | 0.0019336 | 0.0048837
#2 Oil Factors
24 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 8.0059
| PM10 | g/s | 0.023777
| PM2.5 | g/s | 0.023777
1 Hr Periods |  |  | Jan
| Heat Input | MMBtu/hr | 26.37
| NOx | g/s | 0.47465
| SO2 | g/s | 0.005055
Nox emission rate calculation using Vendor data
Nox emissions = 30 ppm (provided)
lbs/mmBtu = ppm*Cd*Fd*(20.9/(20.9-%O2))
Cd is a conversion factor from ppm to lb/dscf at 0% O2 and is specific per pollutant.
Fd is the fuel F conversion factor which is 8710 for natural gas (I don't have it off the top of my head for fuel oil)
So at 70 ppm at 4% O2:
lbs/mmBtu = 12*1.191E-07*8710*(20.9/(20.9-4)) = 0.044 lbs/mmBtu

## Generator Information
Manufacturer Information | [7 empty] | Usage | [5 empty] | Emissions (g/hp-hr)
Generator Rating | Location | Make | Model (Series) | Horsepower | Gross Input (MMBtu/hr) | Fuel | Fuel rate (gal/hr) | Hours/ day | Days / week | Stack Location | Exhaust Temp (F) | Flow rate (cfm) | Diameter (inches) | PM | SO2*
1500 | CUNY | Caterpillar | UL2200 | 4412.1665 | 11.2365 | #2 Diesel | 82 | 1 | 1 | Generator Enclosure on Roof (26ft tall) | 759 | 10908.7 | 8 | 0.03 | 1.2135e-05
2500 | MSK | Caterpillar | UL2200 | 7258.552 | 18.4853 | #2 Diesel | 134.9 | 1 | 1 | Generator Enclosure on Roof (24ft tall) | 915.3 | 19582 | 8 | 0.037 | 1.2135e-05
[11 empty] | 7.1 | lb/gal |  | * | AP-42 Table 3.4-1
[11 empty] | 19300 | btu/lb |  | * | sulfur content of 15ppm (0.0015 percent) (6NYCRR Subpart 225-1.2)
[11 empty] | 2546.699 | (btu/hr)/kw

## Emergency Generator Emissions
MSK-CUNY
| Engines tested at partial load (75%) |  | 1 | hrs/day
|  |  | CUNY | MSK
| Load |  | 75% | 75%
| KW |  | 1500 | 2500
| HP |  | 3309.1249 | 5443.914
| Heat Input (MMbtu/hr) |  | 11.2365 | 18.4853
| Stack ht (ft) |  | 326.25 | 433
| Stack ht (m) |  | 99.441 | 131.9784
| Stack Exhaust Temperature (°F)a |  | 759 | 915.3
| Stack Exhaust Temperature (K) |  | 677.0389 | 763.8722
| Stack Exhaust Diameter (inches) |  | 8 | 8
| Stack Exhaust Diameter (feet) |  | 0.66667 | 0.66667
| Stack Exhaust Flow (ACFM)b |  | 10908.7 | 19582
| Stack Exhaust Velocity (ft/s) |  | 520.8521 | 934.9716
| Stack Exhaust Velocity (m/s) |  | 158.7557 | 284.9794
| Emission rate (g/s) | NOx 1-hr
CO 1-hr
CO 8-hr
SO2 1-hr
|  | SO2 3-hr | 3.7182e-06 | 6.1168e-06
SO2 24-hr
|  | PM10 24-hr | 0.001149 | 0.0023313
|  | PM2.5 24-hr | 0.001149 | 0.0023313
Note
a. It is seen in similar units that there is generally 10% reduction in temperature at 50% as compared to the full load.
b. As seen for similar units, there is generally a 40% reduction in flow rate at 50% load as compared to the full load.

## CUNY Monthly Consumption
[17 empty] | Monthly Usage |  |  | Max Hourly Usage
|  | Lights | Task Lights | Misc Equip | Space Heating | Space Cooling | Heat Reject | Pumps & Aux | Vent Fans | Refrig Display | HT Pump Supplem | Domest Hot Wtr | Ext Usage | Total | Month | Days in Month | BLR (therm) | MMBTU | MMBTU/hr | Therm/hr | MMBTU/hr
Jan | Therm | 0 | 0 | 0 | 19925 | 0 | 0 | 0 | 0 | 0 | 0 | 3668 | 0 | 23593 | 1 | 31 | 23593 | 2359.3 | 3.1711 | 66.8 | 6.68 | 0 | 0 | 0
| Max Therm/Hr | 0 | 0 | 0 | 56.7 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 0 | 64.5 | 2 | 28 | 19298 | 1929.8 | 2.8717 | 50.1 | 5.01 | 0 | 0 | 0
| Day/Hr | [13 empty] | 3 | 31 | 18018 | 1801.8 | 2.4218 | 42.4 | 4.24 | 0 | 0 | 0
| Peak Enduse | [13 empty] | 4 | 30 | 13722 | 1372.2 | 1.9058 | 41.9 | 4.19 | 0 | 0 | 0
| Peak PCT | [13 empty] | 5 | 31 | 9394 | 939.4 | 1.2626 | 43.9 | 4.39 | 0 | 0 | 0
Feb | Therm | 0 | 0 | 0 | 16013 | 0 | 0 | 0 | 0 | 0 | 0 | 3285 | 0 | 19298 | 6 | 30 | 8106 | 810.6 | 1.1258 | 27.6 | 2.76 | 0 | 0 | 0
| Max Therm/Hr | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 0 | 45.2 | 7 | 31 | 8563 | 856.3 | 1.1509 | 22.8 | 2.28 | 0 | 0 | 0
| Day/Hr | [13 empty] | 8 | 31 | 8980 | 898 | 1.207 | 25.5 | 2.55 | 0 | 0 | 0
| Peak Enduse | [13 empty] | 9 | 30 | 8637 | 863.7 | 1.1996 | 26.7 | 2.67 | 0 | 0 | 0
| Peak PCT | [13 empty] | 10 | 31 | 11706 | 1170.6 | 1.5734 | 42.7 | 4.27 | 0 | 0 | 0
Mar | Therm | 0 | 0 | 0 | 14436 | 0 | 0 | 0 | 0 | 0 | 0 | 3582 | 0 | 18018 | 11 | 30 | 14594 | 1459.4 | 2.0269 | 41.9 | 4.19 | 0 | 0 | 0
| Max Therm/Hr | 0 | 0 | 0 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 0 | 39.3 | 12 | 31 | 19499 | 1949.9 | 2.6208 | 51.2 | 5.12 | 0 | 0 | 0
| Day/Hr | [14 empty] | 365 | 164110 | 16411 | 1.8734 |  |  | 0 | 0 | 0
Peak Enduse
Peak PCT
Apr | Therm | 0 | 0 | 0 | 10312 | 0 | 0 | 0 | 0 | 0 | 0 | 3410 | 0 | 13722 |  |  | Monthly Usage Normalized (to Jan) |  |  | Max Usage Normalized (to Jan)
| Max Therm/Hr | 0 | 0 | 0 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 37.4 | Month | Days in Month | BLR (therm) | MMBTU | MMBTU/hr | Therm/hr | MMBTU/hr
| Day/Hr | [13 empty] | 1 | 31 |  | 0 | 1 |  | 1
| Peak Enduse | [13 empty] | 2 | 28 |  | 0 | 0.90559 |  | 0.75
| Peak PCT | [13 empty] | 3 | 31 |  | 0 | 0.7637 |  | 0.63473
May | Therm | 0 | 0 | 0 | 5958 | 0 | 0 | 0 | 0 | 0 | 0 | 3436 | 0 | 9394 | 4 | 30 |  | 0 | 0.601 |  | 0.62725
| Max Therm/Hr | 0 | 0 | 0 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7 | 0 | 39 | 5 | 31 |  | 0 | 0.39817 |  | 0.65719
| Day/Hr | [13 empty] | 6 | 30 |  | 0 | 0.35503 |  | 0.41317
| Peak Enduse | [13 empty] | 7 | 31 |  | 0 | 0.36295 |  | 0.34132
| Peak PCT | [13 empty] | 8 | 31 |  | 0 | 0.38062 |  | 0.38174
Jun | Therm | 0 | 0 | 0 | 4841 | 0 | 0 | 0 | 0 | 0 | 0 | 3265 | 0 | 8106 | 9 | 30 |  | 0 | 0.37829 |  | 0.3997
| Max Therm/Hr | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 24.5 | 10 | 31 |  | 0 | 0.49616 |  | 0.63922
| Day/Hr | [13 empty] | 11 | 30 |  | 0 | 0.63919 |  | 0.62725
| Peak Enduse | [13 empty] | 12 | 31 |  | 0 | 0.82647 |  | 0.76647
| Peak PCT | [14 empty] | 365
Jul | Therm | 0 | 0 | 0 | 5225 | 0 | 0 | 0 | 0 | 0 | 0 | 3338 | 0 | 8563
| Max Therm/Hr | 0 | 0 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 18.7
Day/Hr
Peak Enduse
Peak PCT
Aug | Therm | 0 | 0 | 0 | 5620 | 0 | 0 | 0 | 0 | 0 | 0 | 3360 | 0 | 8980
| Max Therm/Hr | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 21.9
Day/Hr
Peak Enduse
Peak PCT
Sept | Therm | 0 | 0 | 0 | 5352 | 0 | 0 | 0 | 0 | 0 | 0 | 3285 | 0 | 8637
| Max Therm/Hr | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 24.7
Day/Hr
Peak Enduse
Peak PCT
Oct | Therm | 0 | 0 | 0 | 8228 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 0 | 11706
| Max Therm/Hr | 0 | 0 | 0 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 38.6
Day/Hr
Peak Enduse
Peak PCT
Nov | Therm | 0 | 0 | 0 | 11159 | 0 | 0 | 0 | 0 | 0 | 0 | 3435 | 0 | 14594
| Max Therm/Hr | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 0 | 38.1
Day/Hr
Peak Enduse
Peak PCT
Dec | Therm | 0 | 0 | 0 | 15886 | 0 | 0 | 0 | 0 | 0 | 0 | 3613 | 0 | 19499
| Max Therm/Hr | 0 | 0 | 0 | 41.2 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 44.4
Day/Hr
Peak Enduse
Peak PCT

## MSK Month Consumption
[17 empty] | Monthly Usage |  |  | Max Usage
|  | Lights | Task Lights | Misc Equip | Space Heating | Space Cooling | Heat Reject | Pumps & Aux | Vent Fans | Refrig Display | HT Pump Supplem | Domest Hot Wtr | Ext Usage | Total | Month | Days in Month | BLR (therm) | MMBTU | MMBTU/hr | Therm/hr | MMBTU/hr
Jan | Therm | 10136 | 0 | 44891 | 53257 | 24 | 208 | 3319 | 25233 | 0 | 0 | 6307 | 0 | 143375 | 1 | 31 | 59564 | 5956.4 | 8.0059 | 263.7 | 26.37 | 83811 | 8381.1 | 11.2649
| Max Therm/Hr | 23.7 | 0 | 74.8 | 246.3 | 0.8 | 4.3 | 8.1 | 55.1 | 0 | 0 | 17.4 | 0 | 366 | 2 | 28 | 41233 | 4123.3 | 6.1359 | 233.5 | 23.35 | 74538 | 7453.8 | 11.092
| Day/Hr | [13 empty] | 3 | 31 | 26045 | 2604.5 | 3.5007 | 138.4 | 13.84 | 80256 | 8025.6 | 10.7871
| Peak Enduse | [13 empty] | 4 | 30 | 12470 | 1247 | 1.7319 | 109.9 | 10.99 | 75180 | 7518 | 10.4417
| Peak PCT | [13 empty] | 5 | 31 | 7031 | 703.1 | 0.94503 | 73.3 | 7.33 | 73803 | 7380.3 | 9.9198
Feb | Therm | 8930 | 0 | 39985 | 35404 | 14 | 241 | 2936 | 22432 | 0 | 0 | 5829 | 0 | 115771 | 6 | 30 | 5217 | 521.7 | 0.72458 | 15.1 | 1.51 | 68754 | 6875.4 | 9.5492
| Max Therm/Hr | 23.3 | 0 | 73.7 | 216.1 | 0.8 | 4.4 | 7.8 | 53.7 | 0 | 0 | 17.4 | 0 | 336.8 | 7 | 31 | 5000 | 500 | 0.67204 | 14 | 1.4 | 69454 | 6945.4 | 9.3352
| Day/Hr | [13 empty] | 8 | 31 | 4784 | 478.4 | 0.64301 | 13.3 | 1.33 | 70443 | 7044.3 | 9.4681
| Peak Enduse | [13 empty] | 9 | 30 | 4657 | 465.7 | 0.64681 | 37.7 | 3.77 | 69614 | 6961.4 | 9.6686
| Peak PCT | [13 empty] | 10 | 31 | 6320 | 632 | 0.84946 | 84.7 | 8.47 | 75639 | 7563.9 | 10.1665
Mar | Therm | 9407 | 0 | 43215 | 19612 | 168 | 323 | 3113 | 24030 | 0 | 0 | 6433 | 0 | 106301 | 11 | 30 | 15128 | 1512.8 | 2.1011 | 142.7 | 14.27 | 106254 | 10625.4 | 14.7575
| Max Therm/Hr | 21.9 | 0 | 70.7 | 121 | 9.8 | 4.4 | 7.3 | 50.9 | 0 | 0 | 17.4 | 0 | 238.3 | 12 | 31 | 36767 | 3676.7 | 4.9418 | 224 | 22.4 | 81551 | 8155.1 | 10.9612
| Day/Hr | [14 empty] | 365 | 224216 | 22421.6 | 2.5595 |  |  | 929297 | 92929.7 | 10.6084
Peak Enduse
Peak PCT
Apr | Therm | 8508 | 0 | 40855 | 6354 | 411 | 460 | 2856 | 22090 | 0 | 0 | 6116 | 0 | 87650 |  |  | Monthly Usage Normalized (to Jan) |  |  | Max Usage Normalized (to Jan)
| Max Therm/Hr | 21.2 | 0 | 69.8 | 92.5 | 9.9 | 4.4 | 7 | 49.9 | 0 | 0 | 17.4 | 0 | 206.8 | Month | Days in Month | BLR (therm) | MMBTU | MMBTU/hr | Therm/hr | MMBTU/hr
| Day/Hr | [13 empty] | 1 | 31 |  | 0 | 1 |  | 1
| Peak Enduse | [13 empty] | 2 | 28 |  | 0 | 0.76642 |  | 0.88548
| Peak PCT | [13 empty] | 3 | 31 |  | 0 | 0.43726 |  | 0.52484
May | Therm | 7608 | 0 | 39574 | 1175 | 3296 | 273 | 2792 | 20260 | 0 | 0 | 5856 | 0 | 80834 | 4 | 30 |  | 0 | 0.21633 |  | 0.41676
| Max Therm/Hr | 20.8 | 0 | 69 | 56.9 | 20.5 | 4.3 | 6.8 | 49.2 | 0 | 0 | 16.4 | 0 | 170.6 | 5 | 31 |  | 0 | 0.11804 |  | 0.27797
| Day/Hr | [13 empty] | 6 | 30 |  | 0 | 0.090506 |  | 0.057262
| Peak Enduse | [13 empty] | 7 | 31 |  | 0 | 0.083943 |  | 0.053091
| Peak PCT | [13 empty] | 8 | 31 |  | 0 | 0.080317 |  | 0.050436
Jun | Therm | 6404 | 0 | 34354 | 0 | 7171 | 347 | 2699 | 17779 | 0 | 0 | 5217 | 0 | 73971 | 9 | 30 |  | 0 | 0.080791 |  | 0.14297
| Max Therm/Hr | 17.8 | 0 | 67.4 | 0 | 20.3 | 1.4 | 6 | 43.8 | 0 | 0 | 15.1 | 0 | 114.4 | 10 | 31 |  | 0 | 0.1061 |  | 0.3212
| Day/Hr | [13 empty] | 11 | 30 |  | 0 | 0.26244 |  | 0.54115
| Peak Enduse | [13 empty] | 12 | 31 |  | 0 | 0.61727 |  | 0.84945
| Peak PCT | [14 empty] | 365
Jul | Therm | 6000 | 0 | 32408 | 0 | 10803 | 465 | 2777 | 17001 | 0 | 0 | 5000 | 0 | 74454
| Max Therm/Hr | 15.7 | 0 | 632 | 0 | 24 | 1.7 | 5.9 | 40.7 | 0 | 0 | 14 | 0 | 112.5
Day/Hr
Peak Enduse
Peak PCT
Aug | Therm | 6308 | 0 | 33694 | 0 | 9724 | 434 | 2810 | 17473 | 0 | 0 | 4784 | 0 | 75227
| Max Therm/Hr | 17.3 | 0 | 65.8 | 0 | 21.5 | 1.6 | 6 | 42.7 | 0 | 0 | 13.3 | 0 | 111.4
Day/Hr
Peak Enduse
Peak PCT
Sept | Therm | 6758 | 0 | 35122 | 24 | 6690 | 365 | 2721 | 17958 | 0 | 0 | 4633 | 0 | 74271
| Max Therm/Hr | 18.7 | 0 | 68.3 | 24.4 | 27.3 | 4.2 | 6.5 | 46.2 | 0 | 0 | 13.3 | 0 | 132.9
Day/Hr
Peak Enduse
Peak PCT
Oct | Therm | 8363 | 0 | 41431 | 1285 | 1428 | 309 | 2839 | 21269 | 0 | 0 | 5035 | 0 | 81959
| Max Therm/Hr | 20.8 | 0 | 69.9 | 70.7 | 15.6 | 4.5 | 6.9 | 48.9 | 0 | 0 | 14 | 0 | 182.7
Day/Hr
Peak Enduse
Peak PCT
Nov | Therm | 8955 | 0 | 71383 | 9862 | 282 | 358 | 2895 | 22381 | 0 | 0 | 5266 | 0 | 121382
| Max Therm/Hr | 22.2 | 0 | 70.9 | 127.6 | 4.8 | 4.5 | 7.3 | 50.7 | 0 | 0 | 15.1 | 0 | 448.3
Day/Hr
Peak Enduse
Peak PCT
Dec | Therm | 9821 | 0 | 43905 | 30872 | 113 | 255 | 3174 | 24283 | 0 | 0 | 5895 | 0 | 118318
| Max Therm/Hr | 22.8 | 0 | 72.7 | 207.6 | 4.5 | 2.9 | 7.8 | 52.9 | 0 | 0 | 16.4 | 0 | 327.7
Day/Hr
Peak Enduse
Peak PCT